## Registers
Unipi Lite
Holding registers | [6 empty] | v1.0
Register Address |  | Length | R/W | Data Type | Content | Bit Nr. | Category
DEC | HEX
0 | 0x0000 | 1 | R | MixedBits | Digital Inputs |  | Basic
[5 empty] | Digital Input 1 | 0
[5 empty] | Digital Input 2 | 1
[5 empty] | Digital Input 3 | 2
[5 empty] | Digital Input 4 | 3
[5 empty] | Digital Input 5 | 4
[5 empty] | Digital Input 6 | 5
1 | 0x0001 | 1 | RW | MixedBits | Relay outputs |  | Basic
[5 empty] | Relay output 1 | 0
[5 empty] | Relay output 2 | 1
[5 empty] | Relay output 3 | 2
[5 empty] | Relay output 4 | 3
[5 empty] | Relay output 5 | 4
[5 empty] | Relay output 6 | 5
2 | 0x0002 | 2 | RW | uint32 / udint | Counter of Digital Input 1 |  | Basic
4 | 0x0004 | 2 | RW | uint32 / udint | Counter of Digital Input 2 |  | Basic
6 | 0x0006 | 2 | RW | uint32 / udint | Counter of Digital Input 3 |  | Basic
8 | 0x0008 | 2 | RW | uint32 / udint | Counter of Digital Input 4 |  | Basic
10 | 0x000A | 2 | RW | uint32 / udint | Counter of Digital Input 5 |  | Basic
12 | 0x000C | 2 | RW | uint32 / udint | Counter of Digital Input 6 |  | Basic
1010 | 0x03F2 | 1 | RW | uint16 / uint | Debounce time (in 100μs) for DI 1 |  | Advanced
1011 | 0x03F3 | 1 | RW | uint16 / uint | Debounce time (in 100μs) for DI 2 |  | Advanced
1012 | 0x03F4 | 1 | RW | uint16 / uint | Debounce time (in 100μs) for DI 3 |  | Advanced
1013 | 0x03F5 | 1 | RW | uint16 / uint | Debounce time (in 100μs) for DI 4 |  | Advanced
1014 | 0x03F6 | 1 | RW | uint16 / uint | Debounce time (in 100μs) for DI 5 |  | Advanced
1015 | 0x03F7 | 1 | RW | uint16 / uint | Debounce time (in 100μs) for DI 6 |  | Advanced

## Coils
Unipi Lite
Coils |  |  |  | v1.0
Register Address |  | R/W | Content | Category
DEC | HEX
0 | 0x0000 | RW | Relay output 1 | Basic
1 | 0x0001 | RW | Relay output 2 | Basic
2 | 0x0002 | RW | Relay output 3 | Basic
3 | 0x0003 | RW | Relay output 4 | Basic
4 | 0x0004 | RW | Relay output 5 | Basic
5 | 0x0005 | RW | Relay output 6 | Basic

## Description
Unipi Lite
Description |  |  |  |  | v1.0
Check out the Unipi Knowledge base for more information
Byte order
0-LSB, 15-MSB
Default configuration/values
|  | Data | Value | Description
| DI | Counter | 0 | -
|  | Debounce | 0 | 0 ms
| RO | State | 0 | OFF
Note: configuration is not permanently saved, set on each power-on