## Description
Edge E412
Description |  |  |  |  | v1.0
Check out the Unipi Knowledge base for more information
Firmware (re)programming tool - [fwspi]
Debian packages: [unipi-firmware-tools], [unipi-firmware6]
Access to all coils/registers via Unit ID 0 is possible by using formula
address + ((Unit ID - 1)*100)
Byte order
0-LSB, 15-MSB
Default configuration/values
|  | Data | Value | Description
| DI | Counter | 0 | -
|  | Debounce | 50 | 5 ms
|  | Direct Switch | 0 | OFF
| DO | State | 0 | OFF
| MWD | Timeout | 2500 | 2500 ms
|  | Enable | 0 | OFF
Register and Coil starting address
0

## Registers (Unit ID 0)
Edge E412
Holding registers (Unit ID 0) | [6 empty] | v1.0
Register Address |  | Length | R/W | Data Type | Content | Bit Nr. | Category
DEC | HEX
3998 | 0x0F9E | 1 | W | MixedBits | User Programmable LEDs |  | Basic
[5 empty] | User Programmable LED 1 | 0
[5 empty] | User Programmable LED 2 | 1
[5 empty] | User Programmable LED 3 | 2
4000 | 0x0FA0 | 1 | R | uint16 / uint | Storage - Erase cycles used [%] |  | Basic
4001 | 0x0FA1 | 1 | R | uint16 / uint | Storage - Good blocks [%] |  | Basic
4200 | 0x1068 | 1 | R | uint16 / uint | Connection - Mode |  | Basic
4201 | 0x1069 | 1 | R | uint16 / uint | Connection - Network type |  | Basic
4202 | 0x106A | 1 | R | uint16 / uint | Connection - RSSI [dBm] |  | Basic
4203 | 0x106B | 1 | R | uint16 / uint | Connection - Signal quality |  | Basic

## Coils (Unit ID 0)
Edge E412
Coils (Unit ID 0) |  |  |  | v1.0
Register Address |  | R/W | Content | Category
DEC | HEX
3000 | 0x0BB8 | W | User Programmable LED 1 | Basic
3001 | 0x0BB9 | W | User Programmable LED 2 | Basic
3002 | 0x0BBA | W | User Programmable LED 3 | Basic

## Registers (Unit ID 1)
Edge E412
Holding registers (Unit ID 1) | [6 empty] | v1.0
Register Address |  | Length | R/W | Data Type | Content | Bit Nr. | Category
DEC | HEX
0 | 0x0000 | 1 | R | MixedBits | Digital Inputs |  | Basic
[5 empty] | Digital Input 1 | 0
[5 empty] | Digital Input 2 | 1
[5 empty] | Digital Input 3 | 2
[5 empty] | Digital Input 4 | 3
1 | 0x0001 | 1 | RW | MixedBits | Digital Outputs |  | Basic
[5 empty] | Digital Output 1 | 0
[5 empty] | Digital Output 2 | 1
2 | 0x0002 | 1 | RW | MixedBits | Group MasterWatchDog (MWD) Status |  | Advanced
[5 empty] | MWD Enable | 0
[5 empty] | MWD Reboot Detected | 1
3 | 0x0003 | 2 | RW | uint32 / udint | Counter of Digital Input 1 |  | Basic
5 | 0x0005 | 2 | RW | uint32 / udint | Counter of Digital Input 2 |  | Basic
7 | 0x0007 | 2 | RW | uint32 / udint | Counter of Digital Input 3 |  | Basic
9 | 0x0009 | 2 | RW | uint32 / udint | Counter of Digital Input 4 |  | Basic
11 | 0x000B | 1 | RW | uint16 / uint | PWM Duty Cycle of DO 1.1 |  | Basic
12 | 0x000C | 1 | RW | uint16 / uint | PWM Duty Cycle of DO 1.2 |  | Basic
13 | 0x000D | 1 |  |  | Reserved - Do Not Use |  | Reserved
14 | 0x000E | 1 | RW | MixedBits | Synchronised Digital Outputs |  | Advanced
[5 empty] | Synchronised DO 1 | 0
[5 empty] | Synchronised DO 2 | 1
15 | 0x000F | 1 | RW | MixedBits | Synchronised Digital Output Locks |  | Advanced
[5 empty] | Synchronised DO Lock 1 | 0
[5 empty] | Synchronised DO Lock 2 | 1
1000 | 0x03E8 | 1 | R | uint16 / uint | Firmware Version |  | Expert
1001 | 0x03E9 | 1 | R | MixedBits | Number of I/Os |  | Advanced
[5 empty] | Number of DIs | 0 - 7
[5 empty] | Number of DOs | 8 - 15
1002 | 0x03EA | 1 | R | MixedBits | Number of peripherals |  | Advanced
[5 empty] | Number of internal RS485 lines | 0 - 3
[5 empty] | Number of AOs | 4 - 7
[5 empty] | Number of AIs | 8 - 15
1003 | 0x03EB | 1 | R | uint16 / uint | Firmware ID |  | Expert
1004 | 0x03EC | 1 | R | uint16 / uint | Hardware ID |  | Expert
1005 | 0x03ED | 2 | R | uint32 / udint | PCB Serial Number |  | Expert
1007 | 0x03EF | 1 |  |  | Reserved - Do Not Use |  | Reserved
1008 | 0x03F0 | 1 | RW | uint16 / uint | MasterWatchDog (MWD) Timeout (in 1ms) |  | Advanced
1009 | 0x03F1 | 1 | R | uint16 / uint | VRef of MCU |  | Expert
1010 | 0x03F2 | 1 | RW | uint16 / uint | Debounce time (in 100us) for DI 1 |  | Advanced
1011 | 0x03F3 | 1 | RW | uint16 / uint | Debounce time (in 100us) for DI 2 |  | Advanced
1012 | 0x03F4 | 1 | RW | uint16 / uint | Debounce time (in 100us) for DI 3 |  | Advanced
1013 | 0x03F5 | 1 | RW | uint16 / uint | Debounce time (in 100us) for DI 4 |  | Advanced
1014 | 0x03F6 | 1 | RW | MixedBits | Enable DirectSwitch functionality |  | Basic
[5 empty] | Enable DirectSwitch on DI 1 | 0
[5 empty] | Enable DirectSwitch on DI 2 | 1
1015 | 0x03F7 | 1 | RW | MixedBits | Invert DirectSwitch Polarity |  | Basic
[5 empty] | Invert DirectSwitch Polarity on DI 1 | 0
[5 empty] | Invert DirectSwitch Polarity on DI 2 | 1
1016 | 0x03F8 | 1 | RW | MixedBits | Enabled DirectSwitch Toggle |  | Basic
[5 empty] | Enable DirectSwitch Toggle on DI 1 | 0
[5 empty] | Enable DirectSwitch Toggle on DI 2 | 1
1017 | 0x03F9 | 1 | RW | uint16 / uint | Section PWM prescaler |  | Basic
1018 | 0x03FA | 1 | RW | uint16 / uint | Section PWM cycle length |  | Basic

## Coils (Unit ID 1)
Edge E412
Coils (Unit ID 1) |  |  |  | v1.0
Register Address |  | R/W | Content | Category
DEC | HEX
0 | 0x0000 | RW | Digital Output 1 | Basic
1 | 0x0001 | RW | Digital Output 2 | Basic
2 | 0x0002 | R | Digital Input 1 | Basic
3 | 0x0003 | R | Digital Input 2 | Basic
4 | 0x0004 | R | Digital Input 3 | Basic
5 | 0x0005 | R | Digital Input 4 | Basic
1000 | 0x03E8 | RW | MWD reset indication | Advanced
1001 | 0x03E9 |  | Reserved - Do Not Use | Reserved
1002 | 0x03EA | RW | Reset group MCU | Advanced
1003 | 0x03EB | RW | Save current configuration and use on startup | Advanced
1004 | 0x03EC |  | Reserved - Do Not Use | Reserved
1005 | 0x03ED |  | Reserved - Do Not Use | Reserved
1006 | 0x03EE |  | Reserved - Do Not Use | Reserved
1007 | 0x03EF | RW | Enable DirectSwitch on DI 1 | Advanced
1008 | 0x03F0 | RW | Enable DirectSwitch on DI 2 | Advanced
1009 | 0x03F1 | RW | Invert DirectSwitch Polarity on DI 1 | Advanced
1010 | 0x03F2 | RW | Invert DirectSwitch Polarity on DI 2 | Advanced
1011 | 0x03F3 | RW | Enable DirectSwitch Toggle Mode on DI 1 | Advanced
1012 | 0x03F4 | RW | Enable DirectSwitch Toggle Mode on DI 2 | Advanced